## Occupancies
Animal Research | 5 | Station | 0
Anesthesia Workroom (per station) | 5 | Station
Autopsy | 5 | Station
Blood Donors | 5 | Station
Cardiac Catheterization | 5 | Room
Cast Room | 5 | Room
Critical Care | 5 | Bed
Decontamination | 5 | Station
Demonstration (Inservice) | 5 | Station
Dental treatment (per station) | 5 | Operatory
Exam/Treatment | 5 | Room
EEG, ECG, EMG | 5 | Room
EENT | 5 | Room
Emergency Room / Triage | 5 | Room
Induction Room / Holding | 5 | Bed
Intensive Care | 5 | Bed
Isolation (Infectious disease) | 5 | Bed
Laboratory | 5 | Station
Minor Procedures | 5 | Room
Obstetrics: | 5
Delivery Room | 5 | Room (f)
Labor Room | 5 | Room (f)
Labor/Delivery/Recovery (LDR) | 5 | Room (f)
Labor/Delivery/Recovery/Postpartum (LDRP) | 5 | Room (f)
Postpartum Room | 5 | Room (f)
Postpartum Recovery | 5 | Bed
Infant Resuscitation (per station) | 5 | Station
Operating Rooms:
Endo/cysto | 5 | Room
Major O.R. | 5 | Room (h)
Minor O.R. | 5 | Room
Ortho/Neuro O.R. | 5 | Room (h)
Veterinary O.R. | 5 | Room
Observation | 5 | Bed
Pediatric: | 5
Ped. ICU | 5 | Bed
Neonatal ICU (level 3/4) | 5 | Bed
Neonatal ICU (Level 1/2) | 5 | Bed
Nursery | 5 | Bed
Pediatric and Adolescent | 5 | Bed
Psychiatric / Secure | 5 | Bed
Recovery (PACU) (per bed) | 5 | Bed
Patient Room (single) | 5 | Room
Patient Room (Double) | 5 | Room
Respiratory Therapy | 5 | Station
Sterilization / Central Supply | 5 | Station
Trauma Room | 5 | Room

## Medical Air Sizing Calculator
|  |  | Medical Air Source Sizing | [9 empty] | Medical Vacuum Source Sizing | [5 empty] | Medical Vacuum Source Sizing
U.S. Typical Method | [12 empty] | CGA P-2.1 Method | [5 empty] | NFPA 99 Method
Enter the quantity of the units requested: | Counting |  |  | Use |  | Simul. |  | Total | Outlet | Outlet | 0 | lpm for m43 |  | Use |  | Simul. |  | Total | Inlets | Actual | Usage
| Units |  |  | in SCFM |  | Use % |  | Usage | Normal | Count |  |  |  | in SCFM |  | Use % |  | Usage | per AIA | Inlets | Group
Surgical Procedures | [10 empty] | p1 | v1
PreOp Holding | Bed(s) |  | @ | 1.5 | ea. x | 10% | = |  | 1 | 0 | #REF! | 0 | @ | 1 | ea. x | 10% | = |  | 1 | 0 | A
Major Invasive | Room(s) |  | @ | 0.5 | ea. x | 100% | = |  | 2 | 0 | p2 | v2 | @ | 3.5 | ea. x | 100% | = |  | 3 | 0 | A
Minor Invasive | Room(s) |  | @ | 0.5 | ea. x | 75% | = |  | 2 | 0 | #REF! | #REF! | @ | 2 | ea. x | 100% | = |  | 3 | 0 | A
Trauma and Emergency | Room(s) |  | @ | 0.5 | ea. x | 25% | = |  | 1 | 0 | p1 | v1 | @ | 3 | ea. x | 100% | = |  | 3 | 0 | A
Catherization & Lab work | Room(s) |  | @ | 0.5 | ea. x | 25% | = |  | 1 | 0 | #REF! | 0 | @ | 1 | ea. x | 10% | = |  | 2 | 0 | B
Endoscopy | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | p2 | v2 | @ | 2 | ea. x | 100% | = |  | 3 | 0 | A
Recovery | Bed(s) |  | @ | 2 | ea. x | 25% | = |  | 1 | 0 | #REF! | #REF! | @ | 1.5 | ea. x | 50% | = |  | 3 | 0 | A
Tests and Outpatient Procedures
X-ray, CAT, NMR, PET scans | Room(s) |  | @ | 0.5 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0 | B
Dialysis | Bed(s) |  | @ | 0.5 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0 | B
Exam and Minor Treatment | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | B
EEG/EKG | Room(s) |  | @ | 1 | ea. x | 50% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | B
Pulmonary Function | Bed or station |  | @ | 1 | ea. x | 50% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0 | B
Respiratory Care | Bed or station |  | @ | 1 | ea. x | 50% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0 | A
Observation | Bed or station |  | @ | 1.5 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | B
Perinatal and Pediatric
Birthing or LDRP | Room(s) |  | @ | 1 | ea. x | 50% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 100% | = |  | 2 | 0 | A
Delivery Room | Room(s) |  | @ | 0.5 | ea. x | 100% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 100% | = |  | 3 | 0 | A
Nursery | Bed(s) |  | @ | 0.5 | ea. x | 25% | = |  | 2 | 0 |  |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | B
NICU | Bed(s) |  | @ | 1.5 | ea. x | 75% | = |  | 3 | 0 |  |  | @ | 1 | ea. x | 50% | = |  | 3 | 0 | A
Intensive Care
Adult ICU, CCU, etc. | Bed(s) |  | @ | 2 | ea. x | 50% | = |  | 2 | 0 |  |  | @ | 2 | ea. x | 75% | = |  | 3 | 0 | A
Pediatric ICU (Except NICU) | Bed(s) |  | @ | 2 | ea. x | 50% | = |  | 2 | 0 |  |  | @ | 2 | ea. x | 75% | = |  | 3 | 0 | A
Emergency (not surgical) | Bed(s) |  | @ | 2 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 100% | = |  | 1 | 0 | A
Equipment Maintenance
Workrooms | Station(s) |  | @ | 1.5 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 10% | = |  | 1 | 0 | B
Laboratory
Medical Lab Uses | Station(s) |  | @ | 1.5 | ea. x | 25% | = |  | 1 | 0 |  |  | @ | 1.5 | ea. x | 25% | = |  | 1 | 0 | A
Other
Patient rooms | Room(s) |  | @ | 0.5 | ea. x | 10% | = |  | 1 | 0 |  |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | B
|  |  | @ |  | ea. x |  | = |  | 1 | 0 |  |  | @ |  | ea. x |  | =
[7 empty] | Overall Base Total | 0 | [8 empty] | Overall Base Total | 0 | [5 empty] | 
Ventilators | [9 empty] | 0
Ventilator add in | Unit(s) |  | @ | 2 | ea. x | 50% | = | 0 |  |  |  |  | @ | 0.5 | ea. x | 10% | = | 0 | 1 | 0 |  |  |  | Simultaneous
WAGD | [23 empty] | Factor
WAGD (if dual use) | Room(s) | [11 empty] | @ | 2 | ea. x | 100% | = | 0 | 1 | 0 | A | 0 | "A" Terminals |  | 0
[22 empty] | 0 | "B" Terminals |  | 0
|  | Peak Calculated Demand |  | SCFM ( lpm) at 50 psig | [9 empty] | SCFM ( lpm) at 19 inHg | [10 empty] | 0
[26 empty] | 0 | lpm for ae43

## Medical Vac Sizing Calculator
Medical Vacuum Source Sizing
C.G.A. P-2.1 Method
|  | Enter the quantity of the units requested: | Counting |  |  | Use |  | Simul. |  | Total | Outlet | Outlet | 0 | lpm for b43
|  |  | Units |  |  | in SCFM |  | Use % |  | Usage | Normal | Count
Surgical Procedures | [12 empty] | p1 | v1
PreOp Holding |  |  | Bed(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | #REF! | 0
Major Invasive |  |  | Room(s) |  | @ | 3.5 | ea. x | 100% | = |  | 2 | 0 | p2 | v2
Minor Invasive |  |  | Room(s) |  | @ | 2 | ea. x | 100% | = |  | 2 | 0 | #REF! | #REF!
Trauma and Emergency |  |  | Room(s) |  | @ | 3 | ea. x | 100% | = |  | 1 | 0 | p1 | v1
Catherization & Lab work |  |  | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0 | #REF! | 0
Endoscopy |  |  | Room(s) |  | @ | 2 | ea. x | 100% | = |  | 1 | 0 | p2 | v2
Recovery |  |  | Bed(s) |  | @ | 1.5 | ea. x | 50% | = |  | 1 | 0 | #REF! | #REF!
WAGD (If into the Med-Surg. Vacuum) |  |  | Room(s) |  | @ | 2 | ea. x | 100% | =
Tests and Outpatient Procedures
X-ray, CAT, NMR, PET scans |  |  | Room(s) |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0
Dialysis |  |  | Bed(s) |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0
Exam and Minor Treatment |  |  | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0
EEG/EKG |  |  | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0
Pulmonary Function |  |  | Bed or station |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0
Respiratory Care |  |  | Bed or station |  | @ | 1.5 | ea. x | 30% | = |  | 1 | 0
Observation |  |  | Bed or station |  | @ | 1 | ea. x | 10% | = |  | 1 | 0
Perinatal and Pediatric
Birthing or LDRP |  |  | Room(s) |  | @ | 1 | ea. x | 100% | = |  | 1 | 0
Delivery Room |  |  | Room(s) |  | @ | 1 | ea. x | 100% | = |  | 1 | 0
Nursery |  |  | Inlet(s) |  | @ | 1 | ea. x | 10% | = |  | 2 | 0
NICU |  |  | Bed(s) |  | @ | 1 | ea. x | 50% | = |  | 3 | 0
Intensive Care
Adult ICU, CCU, etc. |  |  | Bed(s) |  | @ | 2 | ea. x | 75% | = |  | 2 | 0
Pediatric ICU (Except NICU) |  |  | Bed(s) |  | @ | 2 | ea. x | 75% | = |  | 2 | 0
Emergency (not surgical) |  |  | Bed(s) |  | @ | 1 | ea. x | 100% | = |  | 1 | 0
Equipment Maintenance
Workrooms |  |  | Station(s) |  | @ | 1.5 | ea. x | 10% | = |  | 1 | 0
Laboratory
Medical Lab Uses |  |  | Station(s) |  | @ | 1.5 | ea. x | 25% | = |  | 1 | 0
Other
Patient rooms |  |  | Room(s) |  | @ | 1 | ea. x | 10% | = |  | 1 | 0
[5 empty] | @ |  | ea. x |  | = |  | 1 | 0
[9 empty] | Overall Base Total | 0
Ventilators | [11 empty] | 0
Ventilator add in |  |  | Unit(s) |  | @ | 0.5 | ea. x | 10% | = | 0
| Peak Calculated Demand |  |  | SCFM ( lpm) at 19 inches Hg