## VFD Savings
Customer: | Customer Name
AREA: | Project Name
Enter the data in the Blue boxes and the rest of the sheet will calculate automatically. This chart does not reflect the additional savings from reducing the heat load caused by the motors excess energy usage.
Patton's Medical VFD Energy Analysis
Existing System:
Existing Motor if Different than one replacing | 7.5 |  | ← | Full nameplate Horsepower rating of the motor being used for calculation
Proposed System:
Full Horsepower | 4 |  | ← | Full nameplate Horsepower rating of the motor being used for calculation
Full RPM | 3600 |  | ← | Full nameplate RPM rating of the motor being used for calculation
Hertz | 60 |  | ← | Frequency of supplied electrical power - usually 60hz
Motor Efficiency | 85% |  | ← | Motor efficiency rating
Cost of VFD | 3275 |  | ← | Cost of the VFD
Cost of Motor Upgrade | 0 |  | ← | Cost of any associated motor upgrade.
Cost of Installation | 0 |  | ← | Cost of installation including any control changes
Cost of KWH | 0.095 |  | ← | Cost per KWH of electricity at the facility
Daily Hours of Operation | 24 |  | ← | Hours of daily operation of the motor.
Existing System (no VFD):
Percent of Full RPM |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
HP_full |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Calculated RPM |  | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
RPM_full |  | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
(Calculated RPM / Full RPM)^2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Calculated HP |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Annual KWH |  | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118 | 57661.4118
Annual Cost |  | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341 | 5477.8341
Proposed System (with VFD):
Percent of Full RPM |  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
HP_full |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Calculated RPM |  | 360 | 720 | 1080 | 1440 | 1800 | 2160 | 2520 | 2880 | 3240 | 3600
RPM_full |  | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
(Calculated RPM / Full RPM)^2 |  | 0.01 | 0.04 | 0.09 | 0.16 | 0.25 | 0.36 | 0.49 | 0.64 | 0.81 | 1
Calculated HP |  | 0.04 | 0.16 | 0.36 | 0.64 | 1 | 1.44 | 1.96 | 2.56 | 3.24 | 4
Power Usage |  | 1% | 4% | 9% | 16% | 25% | 36% | 49% | 64% | 81% | 100%
Power Savings |  | 99% | 96% | 91% | 84% | 75% | 64% | 51% | 36% | 19% | 0%
VFD Output Hz |  | 6 | 12 | 18 | 24 | 30 | 36 | 42 | 48 | 54 | 60
Annual KWH with VFD |  | 307.5275 | 1230.1101 | 2767.7478 | 4920.4405 | 7688.1882 | 11070.9911 | 15068.8489 | 19681.7619 | 24909.7299 | 30752.7529
Annual Cost with VFD |  | 29.2151 | 116.8605 | 262.936 | 467.4418 | 730.3779 | 1051.7442 | 1431.5406 | 1869.7674 | 2366.4243 | 2921.5115
Annual Savings with VFD |  | 5448.619 | 5360.9737 | 5214.8981 | 5010.3923 | 4747.4562 | 4426.09 | 4046.2935 | 3608.0667 | 3111.4098 | 2556.3226
Break-Even payback in Years |  | 0.60107 | 0.6109 | 0.62801 | 0.65364 | 0.68984 | 0.73993 | 0.80938 | 0.90769 | 1.0526
Note on G46: Not knowing the demand profile certain assumptions are left up to the facility as to how much demand fluctuates. We control claw vacuum pump speeds from 25Hz-full speed (60Hz). You can make a number of assumptions from the highlighted area as a possible savings and potential payback for the VFD Option.